## Sheet1
|  | Fire Start |  | Location |  |  |  | Fire |  |  |  |  | Utility Facility |  |  | Outage |  |  |  | Suspected Cause
Utility | [5 empty] | Land |  |  |  | Facility | Other |  | Equipment
Name |  |  |  |  | Material at |  |  |  | Suppressing | Identificat |  | Voltage |  |  | Was There |  |  | Suspected Ignition |  |  |  | Contributing
| Date | Time | Latitude | Longitude |  | Use at | Size | Suppressed by |  |  | Comp |  | Involved With | Type |  | Date | Time |  | Equipment /Facility Failure | Contact From Object | Facility Contacted
[5 empty] | Origin | Origin |  |  | Agency | ion | anies | (Volts) | Ignition |  | an Outage |  |  | Cause |  |  |  | Factor
SDG&E | 1/29/20 | 19:00 | 33.4149 | -117.5811 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Camp Pendleton FD | Z100041 |  | 230kV | Lightning Arrestor | Overhead | Yes | 1/29/20 | 19:00 | Equipment/Facility Failure | Other |  |  | Weather
SDG&E | 2/11/20 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Heartland Fire | P477433J | telco | 12kV | Conductor | Overhead | Yes | 2/11/20 | 1:13 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force
SDG&E | 2/26/20 | 0:17 | 32.914 | -116.64 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | P972695 |  | 12kV | Lightning Arrestor | Overhead | Yes | 2/26/20 | 0:17 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SDG&E | 5/17/20 | 8:52 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P515883 |  | 12kV | Conductor | Overhead | Yes | 5/17/20 | 8:52 | Contact From Object | Conductor | Balloons |  | Other
SDG&E | 5/31/20 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Chula Vista | P83770 |  | 12kV | Conductor | Overhead | Yes | 5/31/20 | 1:42 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SDG&E | 6/2/20 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | P111476 |  | 12kv | Conductor | Overhead | Yes | 6/2/20 | 18:00 | Contact From Object |  | Vehicle | Pole | Human Error
SDG&E | 6/3/20 | 11:17 | 33.1234 | -117.025 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Escondido | P714414 |  | 12kv | Transformer | Overhead | Yes | 6/3/20 | 11:17 | Contact From Object |  | Animal | Electric Facility | None
SDG&E | 6/26/20 | 5:50 | 33.3534 | -117.5168 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Camp Pendleton FD | Z222452 |  | 230kV | Conductor | Overhead | Yes | 6/26/20 | 5:50 | Unknown |  |  |  | Unknown
SDG&E | 7/5/20 | 14:08 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SDFR, Cal Fire | P14263 | telco | 12kV | Lightning Arrestor | Overhead | Yes | 7/5/20 | 20:55 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SDG&E | 7/17/20 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P115116 | telco | 12kV | Transformer | Overhead | Yes | 7/17/20 |  | Contact From Object |  | Animal | Electric Facility | None
SDG&E | 7/26/20 | 13:44 | 32.819 | -116.9561 | Vegetation | Urban | Less Than .25 Acres | Customer |  | P101639 |  | 12kV | Fuse | Overhead | Yes | 7/26/20 | 13:44 | Equipment/Facility Failure | Fuse |  |  | Unknown
SDG&E | 7/29/20 | 17:14 | 32.737 | -116.875 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P678395 |  | 12kV | Conductor | Overhead | Yes | 7/29/20 | 17:12 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SDG&E | 8/1/20 | 11:11 | 32.631 | -116.174 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P45248 |  | 12kV | Other | Overhead | Yes | 8/1/20 | 11:10 | Equipment/Facility Failure | Other |  |  | Unknown
SDG&E | 8/18/20 | 13:16 | 32.6248 | -117.096 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Chula Vista | P192585 |  | 12kV | Switch | Overhead | Yes | 8/18/20 | 13:29 | Equipment/Facility Failure | Switch |  |  | Unknown
SDG&E | 8/22/20 | 13:38 | 33.0744 | -116.5773 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P31591 |  | Secondary | Conductor | Overhead | Yes | 8/22/20 | 13:38 | Equipment/Facility Failure | Conductor |  |  | Unknown
SDG&E | 8/31/20 | 14:05 | 33.109 | -117.0055 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Escondido | P310132 |  | 12kV | Conductor | Overhead | Yes | 8/31/20 | 14:05 | Contact From Object | Conductor | Vehicle | Pole | Other
SDG&E | 9/2/20 | 19:30 | 33.362 | -117.136 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P215301 |  | 12kV | Conductor | Overhead | Yes | 9/2/20 | 19:30 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None
SDG&E | 9/4/20 | 20:30 | 33.0658 | -116.8592 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P216155 | telco | 12kV | Conductor | Overhead | Yes | 9/4/20 | 20:30 | Contact From Object |  | Vehicle | Pole | Other
SDG&E | 9/5/20 | 14:30 | 32.793 | -116.967 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Heartland Fire | P194421 |  | 120v | Conductor | Overhead | Yes | 9/5/20 | 14:30 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SDG&E | 9/6/20 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | NCFPD | P319486 |  | 12kV | Transformer | Overhead | Yes | 9/6/20 | 23:00 | Equipment/Facility Failure | Transformer |  |  | None
SDG&E | 9/12/20 | 5:30 | 33.1056 | -117.0002 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | P614833 |  | 12kv | Lightning Arrestor | Overhead | Yes | 9/12/20 | 5:30 | Equipment/Facility Failure | Lightning Arrestor |  |  | None
SDG&E | 9/12/20 | 7:00 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P14263 |  | 12kV | Capacitor Bank | Overhead | Yes | 9/12/20 | 7:00 | Equipment/Facility Failure | Capacitor Bank |  |  | None
SDG&E | 9/17/20 | 10:00 | 33.1101 | -117.2693 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Carlsbad | P202732 |  | 12kV | Conductor | Overhead | Yes | 9/17/20 | 10:00 | Equipment/Facility Failure | Other |  |  | None
SDG&E | 9/30/20 | 10:45 | 33.0547 | -116.8913 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | P619632 |  | Secondary | Conductor | Overhead | Yes | 9/30/20 | 10:45 | Equipment/Facility Failure | Conductor |  |  | Unknown
SDG&E |  | 15:05 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | P612927 | telco | 12kv | Lightning Arrestor | Overhead | No | 1/10/00 |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SDG&E |  | 16:51 | 32.865 | -116.66 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | USFS CNF | P257762 |  | 12kV | Lightning Arrestor | Overhead | Yes | 10/14/20 | 16:55 | Contact From Object |  | Animal | Pole | Outside Force
SDG&E |  | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P270154 |  | 12kv | Other | Overhead | Yes | 11/11/20 | 0:00 | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown
SDG&E |  | 9:10 | 33.104 | -117.121 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | NCFPD | P161627 |  | 12kV | Lightning Arrestor | Overhead | Yes | 11/30/20 | 9:10 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SDG&E | 12/3/20 | 11:56 | 33.176 | -117.1541 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NCFPD | P194669 |  | 12kV | Conductor | Overhead | Yes | 12/3/20 | 11:56 | Equipment/Facility Failure | Pole |  |  | Weather