## 2021 Reportables
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2021-01-01 | 1:15 | 35.883 | -119.2702 | Other | Rural | Less Than .25 Acres | Fire Agency | Earlimart Fire Department | OH-1170389E | AT&T California | 12 kV | Conductor | Overhead | Yes | 2021-01-01 | 0:27 | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | 2021-01-02 | 14:26 | 33.959 | -118.0333 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-869619E | Frontier Communications | 12 kV | Other | Overhead | Yes | 2021-01-02 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-01-04 | 22:36 | 34.4351 | -116.8579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-2155034E | None | 12 kV | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-01-12 | 19:32 | 34.1131 | -116.3923 | Other | Rural | Less Than .25 Acres | Fire Agency | San Bernardino Fire Department | OH-2009982E | None | 12 kV | Other | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Human Error
SCE | 2021-01-12 | 20:42 | 33.8726 | -118.3878 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Redondo Beach Fire Department | OH-1726218E | Frontier Communications | 16 kV | Other | Overhead | Yes | 2021-01-12 | 20:42 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-01-13 | 5:42 | 33.9624 | -118.214 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4351059E | None | 4 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-01-14 | 21:11 | 34.0195 | -118.8108 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1868114E | Crown Castle NG West, Inc | 16 kV | Other | Overhead | Yes | 2021-01-14 | 21:11 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-01-15 | 4:45 | 34.0008 | -117.4313 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-207055S | AT&T California | 12 kV | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | 2021-01-16 | 14:52 | 34.8649 | -118.249 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-826052E | None | 12 kV | Lightning Arrestor | Overhead | No |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Other
SCE | 2021-01-20 | 12:36 | 36.348 | -119.4164 | Other | Urban | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-1012206E | AT&T California | 12 kV | Other | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | 2021-01-21 | 0:10 | 34.1536 | -118.7917 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-1730517E | None | 66 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2021-02-13 | 6:33 | 34.6159 | -117.3565 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-2156930E | None | 33 kV | Conductor | Overhead | Yes | 2021-02-13 | 6:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-02-14 | 20:05 | 34.0551 | -118.1638 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Monterey Park Fire Department | OH-4386113E | None | 16 kV | Other | Overhead | Yes | 2021-02-14 | 20:05 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-02-16 | 8:39 | 34.8193 | -118.2904 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-843713E | None | 12 kV | Switch | Overhead | Yes | 2021-02-16 | 8:39 | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2021-02-17 | 16:03 | 36.2034 | -119.1063 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-4247467E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-02-17 | 14:46 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-02-19 | 12:26 | 33.6943 | -116.4135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-4856174E | None | 12 kV | Conductor | Overhead | Yes | 2021-02-19 | 12:25 | Equipment/Facility Failure | Other |  |  | Outside Force
SCE | 2021-02-21 | 0:04 | 34.0419 | -118.6808 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1408744E | Verizon Wireless; Frontier Communications; Crown Castle NG West, Inc. | 16 kV | Other | Overhead | Yes | 2020-02-21 | 0:04 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-02-21 | 23:16 | 34.2936 | -118.7361 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura Company Fire Department | OH-1473192E | AT&T California | 16 kV | Conductor | Overhead | Yes | 2021-02-21 | 23:33 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-02-22 | 13:00 | 33.8981 | -118.0414 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4245360E | Frontier Communications' | 12 kV | Other | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2021-02-23 | 18:59 | 33.9523 | -118.2535 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire | OH-1777028E | Los Angeles Dept of Water and Power | 16 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-02-24 | 17:35 | 34.781 | -117.2609 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-426330S | Frontier Communications | 12 kV | Capacitor Bank | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-02-28 | 10:39 | 33.7755 | -117.9455 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-718905E | AT&T California | 12 kV | Conductor | Overhead | Yes | 2021-02-28 | 10:38 | Wire-Wire Contact |  |  |  | Weather
SCE | 2021-03-01 | 18:04 | 36.2838 | -119.1677 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-4677499E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-03-01 | 19:44 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-03-17 | 18:32 | 34.688 | -118.1708 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1184317E | Frontier Communication | 12 kV | Transformer | Overhead | Yes | 2021-03-17 | 16:57 | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-03-18 | 20:50 | 33.9149 | -118.2812 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-796721E | None | 16 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-03-19 | 11:19 | N/A | N/A | Other | Rural | Less Than .25 Acres | Unknown |  | Sun Village circuit | None | 12 kV | Conductor | Overhead | Yes |  |  | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2021-03-21 | 9:10 | 34.4275 | -119.0981 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1832446E | Frontier Communications | 16 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-03-26 | 1:42 | 34.2829 | -118.6905 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5437825 | None | 16 kV | Other | Overhead | Yes | 2021-03-26 | 1:42 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-03-31 | 14:06 | 33.7405 | -117.9156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-1360410E | AT&T California | 12 kV | Conductor | Overhead | Yes | 2021-03-31 | 14:06 | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-04-01 | 20:01 | 36.3121 | -119.1702 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4632054E | None | 12 kV | Other | Overhead | Yes | 2021-04-01 | 19:51 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-04-01 | 20:40 | 34.4733 | -117.2231 | Other | Urban | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | OH-2384281E | None | 12 kV | Transformer | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-04-02 | 14:37 | 34.1443 | -116.0843 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4037189E | Frontier Communications | 12 kV | Lightning Arrestor | Overhead | No |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Other
SCE | 2021-04-03 | 9:33 | 34.489 | -117.0114 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4219310E | None | 12 kV | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-04-03 | 11:09 | 36.1387 | -118.9556 | Other | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | 1120693E | None | 66 kV | Other | Overhead | Yes | 2021-04-03 | 10:55 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-04-03 | 21:18 | 33.7287 | -117.1468 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4768419E | None | 12 kV | Other | Overhead | Yes | 2021-04-03 | 19:26 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-04-05 | 19:22 | 35.7233 | -118.1082 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-4778323E | None | 12 kV | Fuse | Overhead | Yes | 2021-04-05 | 15:34 | Equipment/Facility Failure | Fuse |  |  | Other
SCE | 2021-04-05 | 20:57 | 34.483 | -119.7997 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | USDA/CA Forestry | OH-4127954E | None | 16 kV | Conductor | Overhead | Yes | 2021-04-05 | 20:58 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-04-06 | 3:27 | 34.2978 | -119.1817 | Other | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1166198E | AT&T California | 16 kV | Other | Overhead | Yes | 2021-04-06 | 3:38 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2021-04-09 | 12:14 | 34.4938 | -117.2078 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-18978CIT | Frontier Communications;Crown Castle NG West, Inc | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2021-04-10 | 15:35 | 34.1192 | -117.2351 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Highland Fire Department | OH-860549E | None | 12 kV | Conductor | Overhead | Yes | 2021-04-10 | 15:35 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-04-12 | 14:55 | 34.8973 | -118.2913 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1586639E | None | 12 kV | Other | Overhead | Yes | 2021-04-12 | 14:48 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-04-12 | 19:13 | 33.8371 | -117.1456 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-1885770E | None | 33 kV | Conductor | Overhead | Yes | 2021-04-12 | 19:13 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-04-16 | 15:19 | 34.5282 | -117.2359 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | OH-2157461E | None | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-04-25 | 20:49 | 34.4828 | -117.9136 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1875844E | None | 12 kV | Conductor | Overhead | Yes | 2021-04-25 | 21:42 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2021-04-30 | 17:00 | 36.3425 | -119.7086 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4274254E | AT&T California | 12 kV | Conductor | Overhead | Yes | 2021-04-30 | 17:00 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-05-03 | 20:13 | 36.3361 | -119.2868 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Visalia Fire Department | OH-1061311E | None | 12 kV | Conductor | Overhead | Yes | 2021-05-03 | 20:13 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-05-05 | 7:05 | 34.9677 | -118.141 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern City Fire Department | OH-1699778E | AT&T California | 12 kV | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-05-06 | 20:00 | 33.959 | -117.56 | Vegetation | Urban | Less Than .25 Acres | Fire agency | City of Eastvale Fire Department | OH-4695507E | None | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-05-08 | 0:50 | 35.118 | -118.2264 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4041670E | None | 12 kV | Conductor | Overhead | Yes | 2021-05-08 | 0:20 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-05-17 | 17:46 | 36.4248 | -119.0946 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-449608E | None | 12 kV | Conductor | Overhead | Yes | 2021-05-17 | 16:27 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-05-18 | 14:28 | 35.6388 | -118.4039 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4410369E | None | 12 kV | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2021-05-18 | 22:59 | 33.9576 | -118.2396 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4450122E | None | 16 kV | Conductor | Overhead | Yes | 2021-05-18 | 19:30 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-05-19 | 19:05 | 34.198 | -118.9008 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1344496E | Frontier Communications | 16 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-05-19 | 21:32 | 33.8451 | -117.1268 | Other | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE Riverside County Fire Department | OH-4213116E | None | 33 kV | Conductor | Overhead | Yes | 2021-05-25 | 22:03 | Other |  |  |  | Unknown
SCE | 2021-05-21 | 11:41 | 33.748 | -118.3225 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1140432E | AT&T California | 16 kV | Other | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-05-21 | 12:45 | 33.613 | -114.5935 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-4320214E | Frontier Communications | 4 kV | Lightning Arrestor | Overhead | Yes | 2021-05-21 | 12:45 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-05-24 | 5:35 | 35.0003 | -117.6502 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1572879E | Frontier Communications | 4 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | 2021-05-24 | 15:48 | 34.0794 | -117.2591 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-1811364E | None | 12 kV | Conductor | Overhead | Yes | 2021-05-24 | 15:48 | Wire-Wire Contact |  |  |  | Weather
SCE | 2021-05-24 | 16:30 | 34.54 | -117.31 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville City Fire Department | OH-4355423E | Frontier Communications | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-05-25 | 14:05 | 33.818 | -118.2187 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-738900E | None | 12 kV | Fuse | Overhead | Yes | 2021-05-25 | 13:59 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-05-25 | 14:45 | 34.118 | -117.2502 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-688145E | None | 12 kV | Other | Overhead | Yes | 2021-05-25 | 14:03 | Other |  |  |  | Human Error
SCE | 2021-05-25 | 18:58 | 34.0465 | -117.2546 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Loma Linda Fire Department | OH-1595854E | Frontier Communication | 12 kV | Other | Overhead | Yes | 2021-05-25 | 19:47 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-05-26 | 15:28 | 37.3646 | -118.4173 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire & Bishop Fire Department | OH-1569129E | Frontier Communications | 12 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-05-28 | 8:09 | 34.4598 | -117.2824 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-2325891E | Frontier Communications | 12 kV | Transformer | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-05-30 | 0:36 | 35.62 | -117.66 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4552905E | Frontier Communications | 12 kV | Other | Overhead | No |  |  | Other |  |  |  | Other
SCE | 2021-06-01 | 12:11 | 35.1144 | -117.9708 | Other | Rural | Less Than .25 Acres | Fire Agency | Cal City Fire Department | OH-46211S | None | 12 kV | Lightning arrester | Overhead | Yes | 2021-06-21 | 12:30 | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-06-03 | 13:53 | 33.9844 | -117.052 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Yucaipa Fire Department | OH-4311307E | None | 12 kV | Conductor | Overhead | Yes | 2021-06-03 | 13:52 | Contact From Object |  | Balloons | Electric Facility | Other
SCE | 2021-06-07 | 19:38 | 34.4596 | -118.5469 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4239781E | None | 66 kV | Other | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-06-09 | 12:30 | 36.3215 | -119.6507 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1743700E | None | 12 kV | Switch | Overhead | Yes | 6/9/202110: | 10:25 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-06-09 | 16:38 | 34.4369 | -119.7883 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-1256415E | Crown Castle NG West, Inc | 16 kV | Other | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-06-12 | 16:31 | 34.1544 | -117.2969 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-772810E | Frontier Communications | 12 kV | Other | Overhead | Yes | 2021-06-12 | 16:31 | Other |  |  |  | Other
SCE | 2021-06-12 | 17:11 | 34.4489 | -119.7728 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Santa Barbara County Fire Department | OH-4127595E | Frontier Communications | 16 kV | Other | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-06-13 | 20:15 | N/A | N/A | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | Customer Owned, on Trumpet circuit | None | 16 kV | Other | Overhead | No |  |  | Other |  |  |  | Other
SCE | 2021-06-15 | 14:35 | 34.3451 | -119.4148 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Ventura County Fire Department | OH-463451E | None | 16 kV | Other | Overhead | Yes | 2021-06-15 | 15:34 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-06-15 | 16:14 | 33.6638 | -116.9722 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Hemet Fire Agency | OH-4163014E | Frontier Communications | 12 kV | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | 2021-06-15 | 18:00 | 34.3839 | -117.3399 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino Fire Department | OH-2154671E | Frontier Communications | 12 kV | Other | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | 2021-06-15 | 19:11 | 34.4365 | -118.3204 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2329940E | None | 16 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-06-15 | 20:01 | 34.0952 | -117.8465 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2376887E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-06-15 | 20:01 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-06-16 | 15:15 | 34.5071 | -117.2082 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4616677E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-06-16 | 15:15 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error
SCE | 2021-06-16 | 16:35 | 34.142 | -117.3031 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4407988E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-06-16 | 13:53 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-06-18 | 20:30 | 34.8374 | -118.857 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Kern County Fire | OH-7015558 | None | 66 kV | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-06-19 | 8:03 | 34.0278 | -117.72 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2092651E | Frontier Communications | 12 kV | Lightning Arrestor | Overhead | Yes | 2021-06-19 | 8:08 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-06-19 | 21:13 | 36.069 | -119.0097 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4210318E | AT&T California | 12 kV | Conductor | Overhead | Yes | 2021-06-19 | 16:25 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-06-21 | 3:30 | 35.9513 | -117.9109 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-325014S | None | 12 kV | Conductor | Overhead | Yes | 2021-06-21 | 3:30 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-06-22 | 17:00 | N/A | N/A | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4856381E | Frontier Communications | 12 kV | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-06-23 | 6:31 | 34.1869 | -118.1113 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4080223E | Crown Castle NG West, Inc; AT&T California | 16 kV | Conductor | Overhead | Yes | 2021-06-23 | 6:31 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-06-23 | 11:09 | 34.5505 | -117.3266 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville City Fire Department | OH-4135130E | None | 33 kV | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-06-23 | 14:57 | 33.7565 | -116.7328 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Rancho Cucamonga Fire Department | OH-2121121E | Frontier Communications | 12 kV | Other | Overhead | Yes | 2021-06-23 | 14:57 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-06-24 | 16:38 | 33.7051 | 117.1937 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-312403S | None | 12 kV | Conductor | Overhead | Yes | 2021-06-24 | 15:00 | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2021-06-25 | 18:33 | 33.4995 | -117.0536 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1760193E | Frontier Communications | 12 kV | Transformer | Overhead | Yes | 2021-06-25 | 18:33 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-06-25 | 21:06 | 33.8695 | -118.2096 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1809258E | None | 16 kV | Conductor | Overhead | Yes | 2021-06-25 | 19:07 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2021-06-27 | 15:48 | 33.9367 | -116.9829 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Couty Fire Deparment | OH-GT250238 | Frontier Communications | 4 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-06-27 | 21:25 | 33.8482 | -116.5717 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-335255S | Frontier Communications | 33 kV | Other | Overhead | Yes | 2021-06-27 | 20:56 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-06-27 | 20:07 | 34.0805 | -118.0891 | Other | Urban | Less Than .25 Acres | Unknown |  | UG-5311093 | None | 16 kV | Transformer | Underground | Yes | 2021-06-27 | 21:24 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-06-28 | 18:13 | 34.5932 | -118.0583 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Cal Fire | OH-1241247E | None | 12 kV | Conductor | Overhead | Yes | 2021-06-28 | 18:11 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-07-07 | 13:32 | 34.2588 | -119.2488 | Other | Urban | Less Than .25 Acres | Fire Agency | Ventura Fire Department | OH-1746314E | None | 16 kV | Other | Overhead | Yes | 2021-07-07 | 16:07 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-07-07 | 14:30 | 33.921 | -118.1726 | Other | Urban | Less Than .25 Acres | Customer |  | OH-578119E | AT&T California | 4 kV | Conductor | Overhead | Yes | 2021-07-07 | 14:00 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-07-08 | 11:40 | 35.1096 | -118.5211 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4426640E | None | 66 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-07-09 | 18:13 | 33.8678 | -118.1814 | Building | Urban | Less Than .25 Acres | Fire Agency | Long Beach Fire | OH-4083476E | Frontier Communications | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-07-11 | 14:37 | 34.0554 | -118.1741 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-994184E | AT&T California | 4 kV | Conductor | Overhead | Yes | 2021-07-11 | 14:37 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-07-11 | 16:04 | 36.486 | -119.2538 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Woodlake Fire Department | OH-4600860E | None | 12 kV | Conductor | Overhead | Yes | 2021-07-11 | 19:15 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-07-14 | 3:02 | 34.4427 | -119.2486 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1718894E | AT&T California | 16 kV | Conductor | Overhead | Yes | 2021-07-14 | 3:02 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-07-14 | 5:00 | 36.0609 | -118.9929 | Other | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4700916E | None | 12 kV | Conductor | Overhead | Yes | 2021-07-14 | 5:18 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-07-16 | 15:53 | 33.6208 | -117.6844 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | UG-5088702 | None | 12 kV | Other | Underground | Yes | 2021-07-16 | 15:53 | Other |  |  |  | Other
SCE | 2021-07-16 | 17:43 | 33.862869 | -118.372715 | Building | Urban | Less Than .25 Acres | Unknown |  | OH-567325E | Frontier Communications | 16 kV | Other | Overhead | Yes | 2021-07-16 | 17:42 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-07-17 | 9:45 | 34.5034 | -117.3267 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-4134444E | None | 12 kV | Lightning Arrestor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-07-19 | 10:00 | 33.8504 | -117.9908 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-1171929E | None | 12 kV | Lightning Arrestor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-07-20 | 4:00 | 34.3612 | -117.2474 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | California Department of Forestry | OH-4843944E | Frontier Communications | 12 kV | Other | Overhead | Yes | 2021-07-20 | 3:38 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2021-07-20 | 21:31 | 33.9265 | -116.5009 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-4805262E | None | 12 kV | Other | Overhead | Yes | 2021-07-20 | 19:52 | Other |  |  |  | Unknown
SCE | 2021-07-21 | 9:30 | 35.1153 | -117.983 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-525878S | Frontier Communications | 12 kV | Other | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | 2021-07-23 | 0:00 | 34.2044 | -119.0971 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4365411E | None | 16 kV | Other | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Weather
SCE | 2021-07-23 | 10:06 | 35.1326 | -117.9386 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1849026E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-07-23 | 8:14 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-07-23 | 10:47 | 36.0491 | -118.8619 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire; Tulare Fire Department | OH-4390344E | None | 12 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-07-23 | 11:07 | 34.4857 | -117.3807 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-4185387E | None | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-07-24 | 4:46 | 34.1131 | -117.9916 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4323669E | AT&T California | 16 kV | Other | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-07-24 | 16:50 | 34.1062 | -118.0861 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4535766E | AT&T California | 16 kV | Conductor | Overhead | Yes | 2021-07-24 | 17:00 | Equipment/Facility Failure | Lightning Arrestor |  |  | Other
SCE | 2021-07-25 | 11:31 | 35.5061 | -115.4337 | Vegetation | Rural | Less Than .25 Acres | Fire Agency |  | OH-2151267E | None | 33 kV | Conductor | Overhead | Yes | 2021-07-25 | 11:30 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | 2021-07-31 | 14:43 | 34.5383 | -117.3178 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-2156031E | Frontier Communication | 12 kV | Conductor | Overhead | Yes | 2021-07-31 | 14:43 | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-08-02 | 12:19 | 33.875587 | -118.085879 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-M9857Y | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-08-02 | 13:45 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-08-03 | 17:25 | 34.3077 | -118.9243 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4727232E | AT&T California | 16 kV | Conductor | Overhead | Yes | 2021-08-03 | 17:25 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | 2021-08-05 | 7:08 | 33.8346 | -116.4666 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2267109E | None | 12 kV | Other | Overhead | Yes | 413674 | 6:56 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-08-06 | 19:53 | 34.1268 | -117.2478 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-688519E | Frontier Communications | 4 kV | Other | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-08-08 | 21:00 | 34.0696 | -117.7178 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-762697E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-08-08 | 20:14 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-08-09 | 12:19 | 34.143 | -117.2159 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-1859343E | None | 12 kV | Fuse | Overhead | Yes | 2021-08-09 | 10:05 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-08-11 | 14:09 | 36.0882 | -119.1878 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-2041681E | None | 12 kV | Conductor | Overhead | Yes | 2021-08-11 | 13:55 | Contact From Object |  | Other | Electric Facility | Human Error
SCE | 2021-08-13 | 1:58 | 33.818 | -118.2018 | Other | Urban | Less Than .25 Acres | Fire Agency | Long Beach Fire Department | OH-1025074E | Frontier Communications | 4 kV | Other | Overhead | Yes | 2021-08-13 | 16:24 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-08-15 | 17:13 | 36.0671 | -119.0039 | Building | Urban | Less Than .25 Acres | Fire Agency | Porterville Fire Department | OH-1571608E | None | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-08-16 | 15:11 | 34.0746 | -117.2647 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5187337 | None | 12 kV | Transformer | Underground | Yes | 2021-08-16 | 13:51 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2021-08-16 | 16:41 | 34.009211 | -117.411871 | Other | Urban | Less than three (3) meters of linear travel | Unknown |  | OH-689960H | AT&T California | 4 kV | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Fuse |  |  | Other
SCE | 2021-08-18 | 11:01 | 35.7092 | -118.46 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4379279E | Frontier Communications | 12 kV | Other | Overhead | Yes | 2021-08-18 | 11:18 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-08-22 | 12:45 | 34.7619 | -118.2379 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1847352E | None | 12 kV | Transformer | Overhead | Yes | 2021-08-22 | 12:45 | Contact From Object |  | Other | Electric Facility | Other
SCE | 2021-08-24 | 2:54 | 34.4166 | -119.5612 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-4630231E | None | 16 kV | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2021-08-25 | 18:05 | 34.2052 | -119.096 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-280425E | Frontier Communications | 16 kV | Switch | Overhead | Yes | 2021-08-25 | 18:05 | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2021-08-26 | 10:57 | 33.8203 | -118.179 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-12630Y | Frontier Communications | 4 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | 2021-08-26 | 11:46 | 34.4954 | -117.3495 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-1958670E | Frontier Communications | 12 kV | Other | Overhead | No |  |  | Contact From Object |  | Vegetation | Pole | Other
SCE | 2021-08-26 | 21:21 | 34.1439 | -117.8828 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1025796E | Frontier Communications | 12 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-08-27 | 17:03 | 34.078141 | -117.3746 | Other | Urban | Less Than .25 Acres | Fire Agency | San Bernardino Fire Department | OH-4887716E | None | 12 kV | Conductor | Overhead | No |  |  | Vandalism/Theft | Pole |  |  | Other
SCE | 2021-08-28 | 15:27 | 35.9823 | -119.025 | Other | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-529184E | AT&T California | 12 kV | Other | Overhead | Yes | 2021-08-28 | 15:27 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-08-30 | 9:19 | 34.8615 | -116.7505 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | OH-4661020E | None | 12 kV | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | 2021-09-03 | 17:05 | 34.7329 | -118.3078 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-430214E | None | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2021-09-04 | 8:50 | 34.3903 | -118.5251 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-2229424E | AT&T California | 16 kV | Lightning Arrestor | Overhead | Yes | 2021-09-04 | 9:10 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-09-05 | 12:54 | 34.2645 | -118.947 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2177032E | AT&T California | 16 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-09-09 | 22:32 | 34.162183 | -117.564728 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Rancho Cucamonga Fire Department | UG-5385331 | None | 12 kV | Other | Underground | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-09-10 | 12:07 | 34.1924 | -119.1086 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-875232E | None | 12 kV | Conductor | Overhead | Yes | 2021-09-10 | 12:07 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-09-10 | 22:44 | 35.1346 | -117.9543 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4002517E | None | 12 kV | Transformer | Overhead | Yes | 2021-09-10 | 22:44 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-09-12 | 12:28 | 34.02 | -117.4864 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-2039669E | None | 12 kV | Other | Overhead | Yes | 2021-09-12 | 12:28 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2021-09-12 | 20:09 | 33.6788 | -114.6069 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-39179S | Frontier Communications | 12 kV | Transformer | Overhead | Yes | 2021-09-12 | 19:53 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-09-19 | 10:26 | 34.0691 | -118.0044 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | UG-5351883 | None | 16 kV | Transformer | Overhead | Yes | 2021-09-19 | 10:26 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-09-22 | 16:19 | 34.034592 | -117.956725 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1072790E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-09-22 | 16:19 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-09-26 | 16:18 | 0 | 0 | Other | Urban | Less Than .25 Acres | Fire Agency | Tulare Fire Department | OH-277767E | None | 12 kV | Conductor | Overhead | Yes | 2021-09-26 | 17:37 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2021-09-28 | 4:42 | 35.1177 | -118.2272 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4041671E | None | 12 kV | Conductor | Overhead | Yes | 2021-09-28 | 5:03 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-09-30 | 14:08 | 33.7474 | -118.3428 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4579818E | Frontier Communications | 16 kV | Other | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-10-01 | 16:38 | 36.1054 | -118.8451 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL Fire | OH-X15823E | None | 12 kV | Transformer | Overhead | Yes | 2021-10-01 | 18:07 | Equipment/Facility Failure | Transformer |  |  | Human Error
SCE | 2021-10-01 | 18:38 | 34.0516 | -118.073 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-1206523E | None | 16 kV | Other | Overhead | Yes | 2021-10-01 | 18:38 | Other |  |  |  | Other
SCE | 2021-10-06 | 13:23 | 36.2001 | -119.0802 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Lindsay Fire Department | OH-4368824E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-10-06 | 13:23 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2021-10-06 | 13:34 | 36.0551 | -118.9786 | Other | Urban | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4677220E | None | 12 kV | Conductor | Overhead | Yes | 2021-10-06 | 14:28 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2021-10-08 | 8:45 | 36.329183 | -119.351557 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Visalia Fire Department | UG-5059773 | None | 12 kV | Transformer | Underground | Yes | 2021-10-08 | 10:10 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2021-10-11 | 14:05 | 36.3472 | -119.6379 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1280826E | None | 12 kV | Conductor | Overhead | Yes | 2021-10-11 | 12:45 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2021-10-11 | 18:55 | 34.0229 | -118.1559 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4538823E | AT&T California | 16 kV | Conductor | Overhead | Yes | 2021-10-11 | 16:55 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2021-10-11 | 23:13 | 33.8696 | -118.1217 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles Couty Fire Department | OH-M8370Y | Frontier Communications | 12 kV | Other | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-10-14 | 15:47 | 33.8734 | -118.0873 |  | Urban | Less Than .25 Acres | Unknown |  | OH-1577864E | Frontier Communications | 12 kV | Conductor | Overhead | Yes | 2021-10-14 | 15:47 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-10-16 | 10:33 | 34.1956 | -119.1968 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-2177116E | Frontier Communications | 16 kV | Conductor | Overhead | Yes | 2021-10-16 | 10:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2021-10-27 | 11:34 | 37.3651 | -118.4237 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Bishop Fire Department | OH-2055469E | Frontier Communications | 12 kV | Other | Overhead | Yes | 2021-10-27 | 11:34 | Other |  |  |  | Human Error
SCE | 2021-10-28 | 1:29 | 33.850691 | -118.010577 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-1278496E | None | 12 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2021-11-22 | 17:11 | 34.789 | -118.5367 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-707244E | None | 12 kV | Conductor | Overhead | Yes | 2021-11-22 | 17:35 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-11-25 | 11:23 | 33.7634 | -117.9568 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1479213E | AT&T California | 12 kV | Conductor | Overhead | No |  |  | Wire-Wire Contact | Splice/Clamp/Connector |  |  | Weather
SCE | 2021-12-02 | 19:44 | 34.5447 | -118.4347 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | U.S. Forestry | OH-4457956E | AT&T California | 16 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2021-12-16 | 9:58 | 34.4225 | -119.6127 | Other | Rural | Less Than .25 Acres | Fire Agency | Montecito Fire Department | OH-4198828E | Crown Castle NG West Inc.; Frontier Communications | 16 kV | Conductor | Overhead | Yes | 2021-12-16 | 9:58 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2021-12-16 | 9:58 | 34.4225 | -119.6127 | Other | Rural | Less Than .25 Acres | Fire Agency | Montecito Fire Department | OH-4198828E | Crown Castle NG West Inc.; Frontier Communications | 16 kV | Conductor | Overhead | Yes | 2021-12-16 | 9:58 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2021-12-17 | 17:47 | 33.9282 | -118.0243 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1423048E | Frontier Communications | 12 kV | Fuse | Overhead | Yes | 2021-12-17 | 17:47 | Equipment/Facility Failure | Fuse |  |  | Other
SCE | 2021-11-25 | 11:42 | 34.0877 | -117.3708 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Rialto Fire Department | OH-261631S | AT&T California | 12 kV | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | 2021-01-19 | 16:26 | 33.8694 | -118.2784 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1283671E | None | 16 kV | Lightning Arrestor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2021-09-02 | 11:29 | 34.0675 | -117.92 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | West Covina Fire Department | OH-1013799E | Frontier Communications | 12 kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;