## Report
Utility Name | Fire Start | [5 empty] | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations |  |  |  |  | Notes (Optional):
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2017-12-21 | 23:40 | 34.1795 | -118.1338 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-4513407E |  | 120/240 V | Conductor | Overhead | Yes | 2017-12-21 | 23:40 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-12-05 | 11:38 | 33.957 | -117.8613 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-788945H | NEXTG NETWORKS,AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-12-05 | 11:38 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-12-01 | 14:29 | 33.7615 | -117.2667 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-4404592e | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-12-01 | 14:29 | Equipment/Facility Failure | Crossarm |  |  | Unknown
SCE | 2017-11-13 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4059962E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2017-11-11 | 10:32 | 34.4271 | -119.6441 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara Fire Department | OH-4255539E | NEXTG NETWORKS,FRONTIER COMMUNICATIONS | 4 kV | Conductor | Overhead | Yes | 2017-11-11 | 10:32:00 AM | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-11-11 | 3:27 | 34.0045 | -117.6487 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-4019309E |  | 66kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-10-27 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1675192E | FRONTIER COMMUNICATIONS | 16kV | Conductor | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2017-10-18 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside Fire Department | OH-1564666E |  | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-10-16 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside Fire Department | OH-1670014E | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-10-10 | 15:55 | 36.3486 | -119.422 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4621799e | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-10-10 | 15:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2017-10-06 | 12:18 | 34.253 | -118.7684 | Vegetation | Urban | Structure Only | Fire Agency | Simi Valley FD | OH-1539057E | TIME WARNER CABLE | 16kV | Conductor | Overhead | Yes | 2017-10-06 | 12:18 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-10-03 | 11:20 | 35.9693 | -119.2978 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-765636E | AT&T CALIFORNIA | 120/240 V | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-09-29 | 15:09 | 36.3427 | -119.6343 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4478990E | AT&T CALIFORNIA | 120/240 V | Conductor | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2017-09-28 | 20:34 | 33.7486 | -116.9455 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Hemet Fire Department | OH-1743227E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-09-28 | 16:27 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-09-27 | 18:40 | 34.1554 | -118.6977 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-1526413E |  | 120/240 V | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-09-22 | 13:26 | 34.0476 | -117.3985 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernadino FD | OH-801734E | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-09-22 | 13:26 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-09-21 | 17:57 | 33.96 | -116.5449 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside Fire Department | OH-4627373E |  | 12kV | Conductor | Overhead | Yes | 2017-09-21 | 16:03 | Wire-Wire Contact |  |  |  | Unknown
SCE | 2017-09-07 | 21:39 | 33.7472 | -117.8796 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-960075E |  | 12kV | Conductor | Overhead | Yes | 2017-09-07 | 21:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-09-01 | 3:40 | 33.8696 | -117.4369 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-208182S | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-09-01 | 4:17 | Other |  |  |  | Weather | Lighting
SCE | 2017-08-31 | 15:09 | 33.6748 | -117.3374 | Building | Urban | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-4162378E |  | 12kV | Conductor | Overhead | Yes | 2017-08-31 | 15:09 | Unknown |  |  |  | Unknown
SCE | 2017-08-29 | 10:18 | 34.1521 | -117.2713 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernadino FD | OH-4823798E |  | 120/240 V | Conductor | Overhead | Yes | 2017-08-29 | 10:18 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-08-29 | 5:15 | 36.1775 | -119.1703 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-2138742E | FRONTIER COMMUNICATIONS | 120/240 V | Conductor | Overhead | Yes | 2017-08-29 | 5:15 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-08-28 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4649701E | NEXTG NETWORKS | 16kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Unknown
SCE | 2017-08-28 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-795917E |  | 16kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Unknown
SCE | 2017-08-24 | 1:53 | 34.7325 | -118.4202 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | LACFD | Cap Bank 0012887 |  | 12kV | Capacitor Bank | Overhead | No |  |  | Equipment/Facility Failure | Capacitor Bank |  |  | Unknown
SCE | 2017-08-19 | 15:16 | 33.7172 | -117.7349 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-4618946E | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-08-19 | 15:16 | Unknown |  |  |  | Unknown
SCE | 2017-08-14 | 9:34 | 36.3287 | -119.263 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Visalia Fire Department | OH-1030717E |  | 12kV | Conductor | Overhead | Yes | 2017-08-14 | 9:34 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-08-12 | 16:34 | 36.4825 | -119.2449 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAlFire | OH-2272602E |  | 12kV | Conductor | Overhead | Yes | 2017-08-12 | 16:34 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-08-12 | 16:34 | 36.4853 | -119.2407 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAlFire | OH-1806903E |  | 12kV | Conductor | Overhead | Yes | 2017-08-12 | 16:34 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2017-08-12 | 14:37 | 34.0804 | -117.8552 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1255315E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-08-12 | 14:37 | Contact From Object |  | Vehicle | Electric Facility | Unknown
SCE | 2017-08-08 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4179753E |  | 12kV | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown
SCE | 2017-08-08 | 17:12 | 34.659 | -118.1679 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | FC 0151903 |  | 12kV | Fuse | Overhead | Yes | 2017-08-08 | 17:12 | Equipment/Facility Failure | Fuse |  |  | Unknown
SCE | 2017-07-31 | 6:32 | 33.89 | -117.9409 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Fullerton Fire Department | OH-741889E | AT&T CALIFORNIA | 12kV | Transformer | Overhead | Yes | 2017-07-31 | 6:32 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2017-07-30 | 6:11 | 34.8082 | -118.3746 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-1755700E |  | 12kV | Conductor | Overhead | Yes | 2017-07-30 | 6:11 | Unknown |  |  |  | Unknown
SCE | 2017-07-29 | 14:23 | 33.7046 | -117.2344 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-64611S | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-07-29 | 14:23 | Contact From Object |  | Other | Electric Facility | Unknown | Umberlla
SCE | 2017-07-29 | 9:26 | 34.422 | -117.1923 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CalFire | OH-4346574E | FRONTIER COMMUNICATIONS | 120/240 V | Conductor | Overhead | Yes | 2017-07-29 | 9:26 | Unknown |  |  |  | Unknown
SCE | 2017-07-23 | 20:07 | 35.7113 | -119.0664 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County Fire Department | OH-1828420E |  | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-07-20 | 16:56 | 34.1068 | -117.965 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-4314704E | AT&T CALIFORNIA | 66kV | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-07-20 | 16:03 | 33.89 | -117.9409 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-7714455E |  | 12kV | Conductor | Overhead | Yes | 2017-07-20 | 16:03 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-07-13 | 10:08 | 33.9991 | -118.3991 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1596444E |  | 16kV | Conductor | Overhead | Yes | 2017-07-13 | 10:08 | Contact From Object |  | Vegetation | Electric Facility | Human Error | Private Tree Trimmer failed branch into lines
SCE | 2017-07-12 | 12:02 | 36.0368 | -119.0107 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Tulare County Fire Department | OH-4368913E | AT&T CALIFORNIA | 12kV | Lightning Arrestor | Overhead | No |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SCE | 2017-07-11 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CalFire | OH-919465E | FRONTIER COMMUNICATIONS | 2.4kV | Conductor | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2017-07-08 | 10:57 | 33.9184 | -116.5475 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-2329039E |  | 33kV | Conductor | Overhead | Yes | 2017-07-08 | 10:57 | Wire-Wire Contact |  |  |  | Unknown
SCE | 2017-07-07 | 12:00 | 35.7736 | -119.0433 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Kern County Fire Department | OH-1316727E |  | 66kV | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-07-07 | 9:48 | 33.7046 | -117.2344 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Westminister FD | OH-6911688E |  | 12kV | Conductor | Overhead | Yes | 2017-07-07 | 9:48 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-07-03 | 12:41 | 33.6593 | -117.5872 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-4252101E |  | 12kV | Conductor | Overhead | Yes | 2017-07-03 | 12:41 | Contact From Object |  | Other | Electric Facility | Unknown | Model Airplane
SCE | 2017-07-02 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-144184E |  | 16kV | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-06-24 | 11:42 | 34.5442 | -117.9512 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-2338078E |  | 120/240 V | Conductor | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2017-06-19 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Utility |  | 30278 Arrastre Canyon Rd., Acton |  | 33kV | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2017-06-19 | 15:30 | 34.0742 | -118.1363 | Vegetation | Urban | Structure Only | Fire Agency | Alhambra FD | OH-539305H |  | 120/240V | Conductor | Overhead | Yes | 2017-06-19 | 15:30 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-18 | 16:43 | 34.1322 | -117.2066 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ontario Fire Department | Atlantic Avenue and Church Avenue, Highland |  | 12kV | Conductor | Overhead | Yes | 2017-06-18 | 16:43 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-18 | 11:06 | 34.0859 | -117.6419 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ontario Fire Department | 745 E. Deodar St., Ontario |  | 4 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-17 | 20:12 | 33.8101 | -117.9991 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-4008188E | MCI COMMUNICATIONS,TIME WARNER SOUTH | 120/240 V | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-16 | 13:58 | 34.3812 | -118.4156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | Palcerita Canyon and Sand Canyon Rd. in cit of Santa Clarita |  | 16kV | Conductor | Overhead | Yes | 2017-06-16 | 13:58 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-06-16 | 13:30 | 34.4573 | -117.2948 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Hesperia FD | OH-1599742E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-06-16 | 13:30 | Contact From Object |  | Vehicle | Electric Facility | Unknown
SCE | 2017-06-14 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare Fire Department | OH-4155776E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-06-13 | 16:09 | 33.7308 | -116.9223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-4364108e | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-06-13 | 16:09 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-06-12 | 16:49 | 35.771 | -119.2499 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1789955E | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-06-12 | 16:49 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-10 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | CalFire | OH-2261368E |  | 120/240V | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-08 | 12:33 | 34.189 | -118.1586 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-202059E | AT&T CALIFORNIA | 16kV | Conductor | Overhead | Yes | 2017-06-08 | 12:33 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-06-07 | 20:50 | 33.7649 | -118.1543 | Other | Rural | Less Than .25 Acres | Fire Agency | Tulare Fire Department | OH-4427265E |  | 12kV | Conductor | Overhead | Yes | 2017-06-07 | 20:50 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-06-04 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-1757417E |  | 33kV | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown
SCE | 2017-06-03 | 16:31 | 34.8812 | -117.9191 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Edwards Air Force Base Fire Department | Lancaster Boulevard and Work Road, California City |  | 115 kV | Conductor | Overhead | Yes | 2017-06-03 | 16:31 | Equipment/Facility Failure | Crossarm |  |  | Unknown
SCE | 2017-06-03 | 14:56 | 34.4034 | -117.3383 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernadino FD | OH-4344412E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2017-06-02 | 19:41 | 33.8022 | -118.2984 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-1637987E |  | 12kV | Conductor | Overhead | Yes | 2017-06-02 | 19:41 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-06-02 | 16:49 | 33.8026 | -118.2993 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-4219598E |  | 12kV | Conductor | Overhead | Yes | 2017-06-02 | 16:49 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-06-02 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4416566E |  | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-06-01 | 12:30 | 34.0111 | -117.4022 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-4412407E |  | 12kV | Conductor | Overhead | Yes | 2017-06-01 | 12:30 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2017-05-30 | 19:39 | 33.99 | -118.3703 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-969024E | AT&T CALIFORNIA | 4 kV | Conductor | Overhead | Yes | 2017-05-30 | 19:39 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-29 | 5:59 | 34.9067 | -117.0064 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Barstow Fire Department | OH-1543497E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-05-29 | 5:59 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-05-24 | 10:05 | 34.4232 | -117.1775 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CalFire | OH-2300688E | FRONTIER COMMUNICATIONS | 120/240 V | Conductor | Overhead | Yes | 2017-05-24 | 10:05 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-05-23 | 12:07 | 34.4204 | -117.1747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Apple Valley FD | OH-4832950E |  | 12kV | Conductor | Overhead | Yes | 2017-05-23 | 12:07 | Unknown |  |  |  | Unknown
SCE | 2017-05-22 | 11:27 | 34.51 | -117.291 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernadino FD | OH-1966164E |  | 12kV | Conductor | Overhead | Yes | 2017-05-22 | 11:27 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2017-05-20 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-4768465E |  | 12kV | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-20 | 15:24 | 33.7817 | -117.9083 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Garden Grove FD | OH-1405576E | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-05-20 | 15:24 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-20 | 9:43 | 34.0426 | -118.6438 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-788558E | FRONTIER COMMUNICATIONS | 16kV | Conductor | Overhead | Yes | 2017-05-20 | 9:43 | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2017-05-19 | 17:57 | 33.8693 | -117.8315 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Placentia Fire Department | OH-1789272E | VERIZON WIRELESS | 12kV | Conductor | Overhead | Yes | 2017-05-19 | 17:57 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-05-19 | 15:51 | 33.6444 | -117.8574 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Newport Fire Department | OH-4248432E |  | 12kV | Conductor | Overhead | Yes | 2017-05-19 | 15:51 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-15 | 13:54 | 35.427678, | -118.805 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | CalFire | Mile 3, Tower 1 of the Correction-Cummings-Kern River 1 |  | 166kV | Conductor | Overhead | No | 2017-05-15 | 13:54 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-05-14 | 11:15 | 33.6416 | -117.1677 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-2283870E |  | 115 kV | Conductor | Overhead | Yes | 2017-05-14 | 11:15 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-11 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | LACFD | OH-848255E |  | 16kV | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-03 | 7:01 | 33.8718 | -118.2682 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-X5500253 |  | 16kV | Conductor | Overhead | Yes | 2017-05-03 | 7:01 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-05-03 | 5:40 | 34.2645 | -118.769 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-1840416E |  | 16kV | Conductor | Overhead | Yes | 2017-05-03 | 5:40 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-05-01 | 20:04 | 34.1571 | -118.0444 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-X5809E | NEXTG NETWORKS,FRONTIER COMMUNICATIONS | 16kV | Conductor | Overhead | Yes | 2017-05-01 | 20:04 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-05-01 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAlFIre | OH-1580964E |  | 55kV | Conductor | Overhead | No |  |  | Contamination |  |  |  | Unknown | Bird Poop
SCE | 2017-04-29 | 16:08 | 33.8984 | -117.2207 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside Fire Department | OH-312923S | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2017-04-29 | 16:08 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-04-29 | 3:17 | 34.1268 | -118.0735 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Monrovia Fire Department | OH-695124H | AT&T CALIFORNIA | 16kV | Conductor | Overhead | Yes | 2017-04-29 | 3:53 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-04-28 | 23:15 | 33.99 | -118.3703 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | PS533 |  | 16kV | Conductor | Overhead | Yes | 2017-04-28 | 23:15 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-04-28 | 10:59 | 33.9286 | -116.6421 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside Fire Department | OH-1905185E |  | 4 kV | Conductor | Overhead | Yes | 2017-04-28 | 17:00 | Unknown |  |  |  | Unknown
SCE | 2017-04-28 | 10:37 | 36.4356 | -119.1908 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Tulare Fire Department | OH-4600865E | AT&T CALIFORNIA | 12kV | Conductor | Overhead | Yes | 2017-04-28 | 10:37 | Contact From Object |  | Vehicle | Pole | Unknown | Hit guy wire
SCE | 2017-04-23 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Palmdale Fire Department | OH-4336106E | AT&T CALIFORNIA | 12KV | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown
SCE | 2017-04-22 | 11:23 | 35.8628 | -119.2526 | Vegetation | Rural | Structure Only | Self Extinguished |  | OH-1501428E |  | 12KV | Conductor | Overhead | Yes | 2017-04-22 | 11:23 | Unknown |  |  |  | Unknown
SCE | 2017-04-16 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Ventura County FD | OH-4495331E | AT&T CALIFORNIA | 16kV | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-04-09 | 1:51 | 33.99 | -118.3703 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ontario Fire Department | PS 493 |  | 12KV | Conductor | Overhead | Yes | 2017-04-09 | 1:51 | Contact From Object |  | Vehicle | Pole | Unknown
SCE | 2017-03-30 | 14:37 | 34.89 | -117.015 | Vegetation | Rural | Structure Only | Fire Agency | Barstow FD | OH-328443S |  | 12KV | Conductor | Overhead | Yes | 2017-03-30 | 14:37 | Equipment/Facility Failure | Pole |  |  | Weather
SCE | 2017-03-17 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-4493863E |  | 12kV | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2017-03-15 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CalFire | OH-2326555E | FRONTIER COMMUNICATIONS | 12KV | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2017-03-13 | 13:42 | 33.9536 | -118.0656 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Santa Fe Springs Fire Department | OH-4209839E |  | 12kV | Conductor | Overhead | Yes | 2017-03-13 | 13:42 | Contact From Object |  | Vehicle | Pole | Unknown
SCE | 2017-03-11 | 17:22 | 34.1285 | -117.2523 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4067378E | FRONTIER COMMUNICATIONS | 12kV | Lightning Arrestor | Overhead | Yes | 2017-03-11 | 17:22 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SCE | 2017-03-10 | 15:46 | 33.7871 | -117.9123 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Garden Grove FD | OH-2095520E |  | 12KV | Conductor | Overhead | Yes | 2017-03-10 | 15:46 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-02-08 | 2:20 | 33.6897 | -117.8528 | Other | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-1838346E | XO COMMUNICATIONS,VERIZON WIRELESS | 66kV | Conductor | Overhead | Yes | 2017-02-08 | 2:20 | Unknown |  |  |  | Unknown
SCE | 2017-01-31 | 2:10 | 33.99 | -118.3703 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Hesperia FD | PS 522 |  | 115 kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2017-01-28 | 18:15 | 33.99 | -118.3703 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-X5037878 |  | 120/240 V | Conductor | Overhead | Yes | 2017-01-28 | 18:15 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2017-01-14 | 1:21 | 34.2656 | -118.9951 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-802855E | FRONTIER COMMUNICATIONS | 16kV | Conductor | Overhead | Yes | 2017-01-14 | 1:21 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2017-01-13 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-220632S | FRONTIER COMMUNICATIONS | 12KV | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown
Note on A1: Name of utility reporting the event Highlights: Green-data is complete and should be reported. Red/Pink-data is incomplete, and unknown if should be reported. Gray-data set should be excluded.
Note on X1: An Optional Field, list additional information that could be useful when examining data.
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on J2: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;

## CPUC Drop Downs
BVES | Building | Rural | Customer | Capacitor Bank | Padmounted | Contact Between Third Party Facility on Pole and Supply Lines | Animal | Human Error | Yes | Less Than .25 Acres | Communication Facility | Capacitor Bank
Kirkwood Meadows | Other | Urban | Fire Agency | Conductor | Overhead | Contact From Object | Balloons | None | No | .26 - 9.99 Acres | Electric Facility | Conductor
Liberty Energy | Vegetation |  | Self Extinguished | Fuse | Subsurface | Contamination | Other | Other |  | 10 - 99 Acres | Pole | Fuse
PacifiCorp |  |  | Unknown | Lightning Arrestor |  | Equipment/Facility Failure | Vegetation | Outside Force |  | 100 - 299 Acres |  | Insulator
PG&E |  |  | Utility | Other |  | Normal Operation | Vehicle | Unknown |  | 300 - 999 Acres |  | Lightning Arrestor
SCE |  |  |  | Switch |  | Other |  | Weather |  | 1000 - 4999 Acres |  | Pole
SDG&E |  |  |  | Transformer |  | Unknown |  |  |  | Greater than 5000 Acres |  | Guy/Span Wire
[6 empty] | Vandalism/Theft |  |  |  | Less than three (3) meters of linear travel |  | Other
[6 empty] | Wire-Wire Contact |  |  |  | Structure Only |  | Protective Relay
Crossarm
Recloser
Sectionalizer
Splice/Clamp/Connector
Switch
Transformer
Voltage Regulator
Note on G2: To be used when contact between a supply facility and non-supply facility on a pole occurred. Note: This field does not specify which facility caused the contact, only that the contact occurred.
Note on G3: Use when contact from outside object caused the incidnet.
Note on G4: Should be used when outside contaminates effect the utility's facilities. Examples: Smoke caused a phase to phase arc which resulted in a fire. Dirt and salt allowed tracking on an insultor, which caused a crossarm to catch on fire and then resulted in a vegetation fire.
Note on G5: A cessation of normal operation
Note on G6: To be used when the supply facility operated normally. Example: A fuse oprated and material fell onto vegetation and started a fire.
Note on G9: This field would include those fires started from gunshots that broke electric equipment, attempted theft of copper cable, etc.
Note on G10: To be used when to two or more supply conductors contact each other.