## Interactive
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SDG&E | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | O'Side FD | Sta. 580-564 |  | 12kV | Transformer | Padmounted | Yes | 2016-01-03 | 4:30 | Contact From Object |  | Vehicle | Electric Facility | Other
SDG&E | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Escondido FD | P319659 |  | 12kV | Conductor | Overhead | Yes | 2016-01-09 | 4:30 | Contact From Object |  | Vegetation | Electric Facility | Weather
SDG&E | 2016-01-16 | 14:42 | 32.7188 | -116.9745 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | SMG/CALFIRE | P270861 |  | 12kV | Conductor | Overhead | Yes | 2016-01-16 | 14:42 | Equipment/Facility Failure | Conductor | Balloons | Electric Facility | None
SDG&E | 2016-01-31 | 15:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CALFIRE | P714625 |  | 12kV | Conductor | Overhead | Yes | 2016-01-31 | 15:00 | Equipment/Facility Failure | Conductor | Other | Pole | Weather
SDG&E | 2016-02-05 | 9:47 | 33.0739 | -117.0862 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Escondido FD | P418131 |  | 12kV | Other | Overhead | Yes | 2016-02-05 | 9:47 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SDG&E | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P414015 |  | 12kV | Conductor | Overhead | Yes | 2016-02-12 | 19:30 | Vandalism/Theft |  |  |  | Outside Force
SDG&E | 2/18/116 | 14400:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P40825 |  | 12kV | Conductor | Overhead | Yes | 2016-02-18 | 6:00 | Equipment/Facility Failure | Conductor | Vehicle | Pole | None
SDG&E | 2016-03-03 | 6:00 | 32.8472 | -116.942 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Lakeside F.D | P874898 | AT&T and Cox | 12kV | Conductor | Overhead | Yes | 2016-03-03 | 6:30 | Contact From Object |  | Vehicle | Pole | Human Error
SDG&E | 2016-03-11 | 11:40 | 33.1563 | -117.2152 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Vista FD | P615947 |  | 12kV | Conductor | Overhead | Yes | 2016-03-11 | 11:40 | Equipment/Facility Failure | Conductor |  |  | Unknown
SDG&E | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Vista FD | P113372 |  | 12kV | Conductor | Overhead | Yes | 2016-04-06 | 10:38 | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error
SDG&E | 2016-04-16 | Unknown | 33.2243 | -117.3683 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Unknown | Z29145 (TL 690, C198) |  | 12kV | Conductor | Overhead | Yes | 2016-04-16 |  | Wind/Equipment/Facility Failure | Conductor | Vegetation |  | Weather
SDG&E | 2016-06-12 | Unknown | 33.094 | -117.043 | Vegetation | Urban | Less Than .25 Acres | Utility | Utility | P712531 |  | 12kV | Conductor | Overhead |  |  |  | Contact from Object |  | Balloons | Electric Facility | None
SDG&E | 2016-06-14 | 6:05 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P370041 | AT&T | 12kV | Conductor | Overhead | Yes | 2016-06-14 | 6:05 | Contact From Object |  | Vehicle | Pole | Outside Force
SDG&E | 2016-06-23 | 15:00 | 32.8058 | -116.961 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | El Cajon FD | P166454 |  | 12kV | Conductor | Overhead | Yes | 2016-06-23 | 15:00 | Contact From Object | Lightning Arrestor | Animal | Electric Facility | Outside Force
SDG&E | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P112086 |  | 12kV | Other | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector | Other |  | Human Error
SDG&E | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P775960 |  | 12kV | Capacitor Bank | Overhead | Yes | 2016-07-02 | 7:51 | Equipment/Facility Failure | Capacitor Bank | Other |  | None
SDG&E | 2016-07-11 | 10:27 | 33.2719 | -117.1826 | Vegetation | Urban | Less Than .25 Acres | Customer | CALFIRE | P228931 C 520 |  | 12kv | Conductor | Overhead | Yes | 2016-07-11 | 10:27 | Contact From Object | Other | Other | Electric Facility
SDG&E | 2016-07-11 | 13:19 | 33.1146 | -116.5843 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P412648 C221 | None | 12kV | Lightning Arrestor | Overhead | Yes | 2016-07-11 | 13:19 | Equipment/Facility Failure | Lightning Arrestor | Other
SDG&E | 2016-07-22 | Unknown | 33.2015 | -116.9352 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P212466 |  | 25kV | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Unknown
SDG&E | 2016-07-29 | 10:57 | 33.071 | -116.7424 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P416995 |  | 12kv | Conductor | Overhead | Yes | 2016-07-29 |  | Equipment/Facility Failure | Conductor | Other
SDG&E | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Fallbrook Fire | P115869 |  | 12kV | Conductor | Overhead | Yes | 2016-07-31 | 13:43 | Contact From Object | Recloser | Vegetation | Electric Facility | Unknown
SDG&E | 2016-08-27 | 12:43 | 33.1371 | -117.0761 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P315560 |  | 12kV | Conductor | Overhead | Yes | 2016-08-27 | 12:43 | Contact From Object | Fuse | Balloons | Electric Facility | Unknown
SDG&E | 2016-09-23 | 11:25 | 32.738 | -116.7333 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P101347 |  | 12kV | Transformer | Overhead | Yes | 2016-09-23 | 11:25 | Equipment/Facility Failure | Transformer | Other |  | None
SDG&E | 2016-09-27 | unknown | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE |  |  | 12kV | Fuse | Overhead | No |  |  | Contact From Object |  |  |  | Unknown
SDG&E | 2016-09-29 |  | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | SMG/CALFIRE | P26106 |  | 12kV | Conductor | Overhead | No |  |  | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force
SDG&E | 2016-09-29 | 8:14 | 33.1714 | -117.3158 | Vegetation | Urban | Less Than .25 Acres | Utility |  | Z524971 | none | 230kV | Conductor | Overhead | No |  |  | Unknown |  |  |  | Unknown
SDG&E | 2016-10-08 | 10:53 | 33.3019 | -117.0974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Valley Center | Z811329 |  | 230kv | Conductor | Overhead | No |  |  | Contact From Object | Switch | Other | Electric Facility | Other
SDG&E | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P114079 |  | 12kV | Conductor | Overhead | No |  |  |  | Transformer | Other
SDG&E | 2016-11-02 | 10:30 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P175475 |  | 12kV | Conductor | Overhead | Yes | 2016-11-02 | 10:30 | Equipment/Facility Failure | Splice/Clamp/Connector | Other |  | None
SDG&E | 2016-11-12 | 20:30 | 32.6258 | -116.9375 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Chula Vista Fire | P85952 |  | 12kV | Lightning Arrestor | Overhead | Yes | 2016-11-12 | 18:34 | Equipment/Facility Failure | Lightning Arrestor | Other
Other
Other
Other
Other
Other
Other
Other
Other
Other
Other
Other
Other
Other
Note on A2: Name of utility reporting the event
Note on X2: An Optional Field, list additional information that could be useful when examining data.
Note on B3: Date the event started (Use MM/DD/YY when inputting dates)
Note on C3: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D3: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E3: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F3: Material involved in the initial fueling of the fire;
Note on G3: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H3: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I3: Is who suppressed the fire
Note on J3: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on K3: Utility’s description of the pole and/or equipment involved.
Note on L3: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M3: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N3: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O3: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P3: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q3: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R3: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S3: The suspected cause of the ignition;
Note on T3: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U3: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V3: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W3: Factors that contributed to the ignition;

## Drop Downs
BVES | Building | Rural | Customer | Capacitor Bank | Padmounted | Contact Between Third Party Facility on Pole and Supply Lines | Animal | Human Error | Yes | Less Than .25 Acres | Communication Facility | Capacitor Bank
Kirkwood Meadows | Other | Urban | Fire Agency | Conductor | Overhead | Contact From Object | Balloons | None | No | .26 - 9.99 Acres | Electric Facility | Conductor
Liberty Energy | Vegetation |  | Self Extinguished | Fuse | Subsurface | Contamination | Other | Other |  | 10 - 99 Acres | Pole | Fuse
PacifiCorp |  |  | Unknown | Lightning Arrestor |  | Equipment/Facility Failure | Vegetation | Outside Force |  | 100 - 299 Acres |  | Insulator
PG&E |  |  | Utility | Other |  | Normal Operation | Vehicle | Unknown |  | 3000 - 999 Acres |  | Lightning Arrestor
SCE |  |  |  | Switch |  | Other |  | Weather |  | 1000 - 4999 Acres |  | Pole
SDG&E |  |  |  | Transformer |  | Unknown |  |  |  | Greater than 5000 Acres |  | Guy/Span Wire
[6 empty] | Vandalism/Theft |  |  |  | Less than three (3) meters of linear travel |  | Other
[6 empty] | Wire-Wire Contact |  |  |  | Structure Only |  | Protective Relay
Crossarm
Recloser
Sectionalizer
Splice/Clamp/Connector
Switch
Transformer
Voltage Regulator
Note on G2: To be used when contact between a supply facility and non-supply facility on a pole occurred. Note: This field does not specify which facility caused the contact, only that the contact occurred.
Note on G3: Use when contact from outside object caused the incidnet.
Note on G4: Should be used when outside contaminates effect the utility's facilities. Examples: Smoke caused a phase to phase arc which resulted in a fire. Dirt and salt allowed tracking on an insultor, which caused a crossarm to catch on fire and then resulted in a vegetation fire.
Note on G5: A cessation of normal operation
Note on G6: To be used when the supply facility operated normally. Example: A fuse oprated and material fell onto vegetation and started a fire.
Note on G9: This field would include those fires started from gunshots that broke electric equipment, attempted theft of copper cable, etc.
Note on G10: To be used when to two or more supply conductors contact each other.